## Ny Ellebjergn
Tid | Intensitet | [5 empty] | Ws,kritisk | [6 empty] | 43 |  |  |  |  | stofkoncentration indløb | 0.005
(min) | (µm/s) | µm per 10 min | m³ for 20 ha/10min | Vådt bassin m² | vandhøjde m | Areal | h | Vbassin | Qind | Ws, kritisk, cm/s | Qud | % tilbageholdelse | bassinkoncentration t0 | tilført TSS gr | TSS bassin gr/m³ | sedimentation i tidsskridt TSS gr/m³ | tilbage i bassin | fjernet uden sedimentation | fjernet ved overløb | Estimat af Benz(A)Pyren i udløbsvand
0 | 0.62956 | 377.7339 | 1.0199 | 265 | 0.5 | 529 | 0.5 | 79.5 | 0.0016998 | 0.0010691 | 1 | 0.98 | 0 | 43.8549 | 0.16549 | 0.16218 | 0.8771 | 43 | 0.0033098 | 3.8486e-07
10 | 0.65694 | 394.1664 | 1.0642 | 265.0199 | 0.50098 | 529 | 0.50098 | 79.506 | 0.0017737 | 0.0011177 | 1 | 0.98 | 0.87379 | 45.7627 | 0.17597 | 0.17245 | 0.93273 | 43 | 0.0035195 | 4.0924e-07
20 | 0.68735 | 412.4077 | 1.1135 | 265.0841 | 0.5011 | 529 | 0.5011 | 79.5252 | 0.0018558 | 0.0011694 | 1 | 0.97 | 0.92921 | 47.8805 | 0.18413 | 0.17861 | 1.4643 | 43 | 0.0055239 | 6.4231e-07
30 | 0.72132 | 432.7937 | 1.1685 | 265.1976 | 0.50132 | 529 | 0.50132 | 79.5593 | 0.0019476 | 0.0012272 | 1 | 0.97 | 1.4588 | 50.2474 | 0.19497 | 0.18912 | 1.5512 | 43 | 0.0058492 | 6.8013e-07
40 | 0.75959 | 455.7512 | 1.2305 | 265.3662 | 0.50164 | 529 | 0.50164 | 79.6099 | 0.0020509 | 0.0012923 | 1 | 0.97 | 1.5453 | 52.9127 | 0.20522 | 0.19906 | 1.6337 | 43 | 0.0061566 | 7.1588e-07
50 | 0.80305 | 481.8322 | 1.3009 | 265.5967 | 0.50207 | 529 | 0.50207 | 79.679 | 0.0021682 | 0.0013663 | 1 | 0.96 | 1.6276 | 55.9407 | 0.21675 | 0.20808 | 2.3027 | 43 | 0.00867 | 1.0081e-06
60 | 0.85294 | 511.7643 | 1.3818 | 265.8977 | 0.50264 | 529 | 0.50264 | 79.7693 | 0.0023029 | 0.0014511 | 1 | 0.96 | 2.2941 | 59.4158 | 0.23208 | 0.2228 | 2.4684 | 43 | 0.0092833 | 1.0794e-06
70 | 0.91088 | 546.5279 | 1.4756 | 266.2794 | 0.50336 | 529 | 0.50336 | 79.8838 | 0.0024594 | 0.0015497 | 1 | 0.96 | 2.4591 | 63.4519 | 0.24753 | 0.23762 | 2.6364 | 43 | 0.009901 | 1.1513e-06
80 | 0.97913 | 587.4789 | 1.5862 | 266.755 | 0.50426 | 529 | 0.50426 | 80.0265 | 0.0026437 | 0.0016658 | 1 | 0.96 | 2.6265 | 68.2063 | 0.26554 | 0.25491 | 2.8333 | 43 | 0.010621 | 1.235e-06
90 | 1.0609 | 636.5513 | 1.7187 | 267.3412 | 0.50537 | 529 | 0.50537 | 80.2024 | 0.0028645 | 0.001805 | 1 | 0.96 | 2.8227 | 73.9036 | 0.287 | 0.27552 | 3.0691 | 43 | 0.01148 | 1.3349e-06
100 | 1.161 | 696.6101 | 1.8808 | 268.0599 | 0.50673 | 529 | 0.50673 | 80.418 | 0.0031347 | 0.0019753 | 1 | 0.95 | 3.0576 | 80.8764 | 0.31312 | 0.29746 | 4.1967 | 43 | 0.015656 | 1.8204e-06
110 | 1.2868 | 772.1004 | 2.0847 | 268.9408 | 0.50839 | 529 | 0.50839 | 80.6822 | 0.0034745 | 0.0021893 | 1 | 0.94 | 4.181 | 89.6409 | 0.34886 | 0.32793 | 5.6293 | 43 | 0.020931 | 2.4339e-06
120 | 1.4506 | 870.3412 | 2.3499 | 270.0254 | 0.51045 | 529 | 0.51045 | 81.0076 | 0.0039165 | 0.0024679 | 1 | 0.91 | 5.6084 | 101.0466 | 0.39498 | 0.35943 | 9.5989 | 43 | 0.035548 | 4.1335e-06
130 | 1.6739 | 1004.3608 | 2.7118 | 271.3754 | 0.513 | 529 | 0.513 | 81.4126 | 0.0045196 | 0.0028479 | 1 | 0.9 | 9.5634 | 116.6063 | 0.46493 | 0.41843 | 12.617 | 43 | 0.046493 | 5.4061e-06
140 | 2 | 1199.9954 | 3.24 | 273.0871 | 0.51623 | 529 | 0.51623 | 81.9261 | 0.0054 | 0.0034026 | 1 | 0.9 | 12.5705 | 139.3195 | 0.5562 | 0.50058 | 15.189 | 43 | 0.05562 | 6.4674e-06
150 | 2.529 | 1517.3936 | 4.097 | 275.3271 | 0.52047 | 529 | 0.52047 | 82.5981 | 0.0068283 | 0.0043026 | 1 | 0.9 | 15.1334 | 176.1694 | 0.69482 | 0.62534 | 19.1303 | 43 | 0.069482 | 8.0793e-06
160 | 3.5663 | 2139.7777 | 5.7774 | 278.4241 | 0.52632 | 529 | 0.52632 | 83.5272 | 0.009629 | 0.0060674 | 1 | 0.89 | 19.0608 | 248.4282 | 0.96073 | 0.85505 | 29.4238 | 43 | 0.10568 | 1.2288e-05
170 | 6.7941 | 4076.4433 | 11.0064 | 283.2015 | 0.53535 | 529 | 0.53535 | 84.9604 | 0.018344 | 0.011559 | 1 | 0.88 | 29.3181 | 473.2751 | 1.7747 | 1.5617 | 60.3112 | 43 | 0.21296 | 2.4763e-05
180 | 23.2252 | 13935.0993 | 37.6248 | 293.2079 | 0.55427 | 529 | 0.55427 | 87.9624 | 0.062708 | 0.039514 | 1 | 0.5 | 60.0982 | 1617.865 | 5.7228 | 2.8614 | 838.9816 | 43 | 2.8614 | 0.00033272
190 | 6.7941 | 4076.4433 | 11.0064 | 329.8326 | 0.6235 | 529 | 0.6235 | 98.9498 | 0.018344 | 0.011559 | 1 | 0.89 | 836.1202 | 473.2751 | 3.9699 | 3.5332 | 144.0335 | 43 | 0.43669 | 5.0778e-05
200 | 3.5663 | 2139.7777 | 5.7774 | 339.839 | 0.64242 | 529 | 0.64242 | 101.9517 | 0.009629 | 0.0060674 | 1 | 0.88 | 143.5968 | 248.4282 | 1.1536 | 1.0151 | 47.043 | 43 | 0.13843 | 1.6096e-05
210 | 2.529 | 1517.3936 | 4.097 | 344.6164 | 0.65145 | 529 | 0.65145 | 103.3849 | 0.0068283 | 0.0043026 | 1 | 0.88 | 46.9046 | 176.1694 | 0.64731 | 0.56963 | 26.7689 | 43 | 0.077677 | 9.0322e-06
220 | 2 | 1199.9954 | 3.24 | 347.7134 | 0.6573 | 529 | 0.6573 | 104.314 | 0.0054 | 0.0034026 | 1 | 0.9 | 26.6912 | 139.3195 | 0.47744 | 0.42969 | 16.6011 | 43 | 0.047744 | 5.5516e-06
230 | 1.6739 | 1004.3608 | 2.7118 | 349.9534 | 0.66154 | 529 | 0.66154 | 104.986 | 0.0045196 | 0.0028479 | 1 | 0.94 | 16.5533 | 116.6063 | 0.38051 | 0.35768 | 7.9896 | 43 | 0.02283 | 2.6547e-06
240 | 1.4506 | 870.3412 | 2.3499 | 351.6652 | 0.66477 | 529 | 0.66477 | 105.4996 | 0.0039165 | 0.0024679 | 1 | 0.94 | 7.9667 | 101.0466 | 0.30999 | 0.29139 | 6.5408 | 43 | 0.0186 | 2.1627e-06
250 | 1.2868 | 772.1004 | 2.0847 | 353.0151 | 0.66733 | 529 | 0.66733 | 105.9045 | 0.0034745 | 0.0021893 | 1 | 0.95 | 6.5222 | 89.6409 | 0.2724 | 0.25878 | 4.8082 | 43 | 0.01362 | 1.5837e-06
260 | 1.161 | 696.6101 | 1.8808 | 354.0998 | 0.66938 | 529 | 0.66938 | 106.2299 | 0.0031347 | 0.0019753 | 1 | 0.96 | 4.7945 | 80.8764 | 0.24194 | 0.23226 | 3.4268 | 43 | 0.0096776 | 1.1253e-06
270 | 1.0609 | 636.5513 | 1.7187 | 354.9806 | 0.67104 | 529 | 0.67104 | 106.4942 | 0.0028645 | 0.001805 | 1 | 0.96 | 3.4172 | 73.9036 | 0.21782 | 0.2091 | 3.0928 | 43 | 0.0087127 | 1.0131e-06
280 | 0.97913 | 587.4789 | 1.5862 | 355.6993 | 0.6724 | 529 | 0.6724 | 106.7098 | 0.0026437 | 0.0016658 | 1 | 0.97 | 3.0841 | 68.2063 | 0.20042 | 0.19441 | 2.1387 | 43 | 0.0060127 | 6.9915e-07
290 | 0.91088 | 546.5279 | 1.4756 | 356.2855 | 0.67351 | 529 | 0.67351 | 106.8856 | 0.0024594 | 0.0015497 | 1 | 0.98 | 2.1327 | 63.4519 | 0.18408 | 0.1804 | 1.3117 | 43 | 0.0036816 | 4.2809e-07
300 | 0.85294 | 511.7643 | 1.3818 | 356.7611 | 0.67441 | 529 | 0.67441 | 107.0283 | 0.0023029 | 0.0014511 | 1 | 0.98 | 1.308 | 59.4158 | 0.17021 | 0.1668 | 1.2145 | 43 | 0.0034042 | 3.9583e-07
310 | 0.80305 | 481.8322 | 1.3009 | 357.1429 | 0.67513 | 529 | 0.67513 | 107.1429 | 0.0021682 | 0.0013663 | 1 | 0.98 | 1.2111 | 55.9407 | 0.16003 | 0.15682 | 1.143 | 43 | 0.0032005 | 3.7215e-07
320 | 0.75959 | 455.7512 | 1.2305 | 357.4438 | 0.6757 | 529 | 0.6757 | 107.2331 | 0.0020509 | 0.0012923 | 1 | 0.98 | 1.1398 | 52.9127 | 0.15122 | 0.1482 | 1.0811 | 43 | 0.0030244 | 3.5167e-07
330 | 0.72132 | 432.7937 | 1.1685 | 357.6744 | 0.67613 | 529 | 0.67613 | 107.3023 | 0.0019476 | 0.0012272 | 1 | 0.98 | 1.078 | 50.2474 | 0.1435 | 0.14063 | 1.0265 | 43 | 0.00287 | 3.3372e-07
340 | 0.68735 | 412.4077 | 1.1135 | 357.8429 | 0.67645 | 529 | 0.67645 | 107.3529 | 0.0018558 | 0.0011694 | 1 | 0.99 | 1.0236 | 47.8805 | 0.13666 | 0.1353 | 0.48904 | 43 | 0.0013666 | 1.5891e-07
350 | 0.65694 | 394.1664 | 1.0642 | 357.9564 | 0.67667 | 529 | 0.67667 | 107.3869 | 0.0017737 | 0.0011177 | 1 | 0.99 | 0.48768 | 45.7627 | 0.12921 | 0.12791 | 0.4625 | 43 | 0.0012921 | 1.5024e-07
|  |  | 129.0207 | [5 empty] | 0.21503 |  |  | 0.93306 |  | 5547.888 |  |  |  | 1548 | 4.2969 | 1.3879e-05
|  |  | tømningstid (timer) | 0.25821
[18 empty] | tilbageholdelse | 0.99722
[18 empty] | koncetration af TSS | 0.11936
[18 empty] | Est. Koncentration af Bisphenol a | 0.0011936
Note on AA39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: anvendes til resten af tømningstiden